## Slide 1: PFAS Remediation: Navigating Challenges, Exploring Technologies, and Envisioning the Future.
Adam Farahani
March 2024

## Slide 2: SciDev A leading provider of water treatment solutions and chemical services
Markets
      Water Treatment
      PFAS Treatment
      Infrastructure and Construction
      Mining and Mineral Processing
      Oil and Gas
  What we do
      Develop and deliver tailored permanent, temporary & mobile water treatment systems
      Reduce waste, OPEX costs and minimise environmental risk
  How we do it
      Innovative water treatment technology
      Industry-leading toolkit of PFAS treatment technology.
      Build Own Operate and Design & Construct commercial models
  Leading PFAS treatment technology-FluorofIX™
      Advanced Ion Exchange systems capable of treated water for the sum of PFAS to <0.2ng/L
      Capable of removing both Short and Long chain PFAS
      RegenIX™ SciDev’s regenerable Ion-Exchange (IX) resin technology to reduce OPEX costs

## Slide 3: SciDev and PFAS
> 7 billion litres
treated to date
SciDev’s Technology
      Treats both short and long-chain analytes
      Commercialised PFAS technology treating to the lowest reportable level available
      Modular and adaptable to changing site conditions
35 PFAS impacted sites remediated
First company to treat below the detectable limit of 0.2ng/L
First PFAS mobile treatment licence granted in NSW
First company in VIC to continuously discharge to the environment
First company in WA to treat and release in a drinking water catchment area
3

## Slide 4: Some NEWS from the last few days….

## Slide 5: Per- and Polyfluoroalkyl Substances (PFAS)
A class of man-made (synthetic) chemicals
Widely used in industrial processes and consumer products
Studies on PFAS have found links between higher exposures and impacts on human health.
PFAS do not break down in the environment, thus earning the name “forever chemicals.”
Became popular because they repel oil and water, are temperature resistant, and reduce friction

## Slide 6: Most Common PFAS
      PerFluoroOctanoic Acid (PFOA)
      PerFluoroOctaneSulfonic Acid (PFOS)
      PolyTetraFluoroEthylene (PTFE)
Other examples of PFAS
6:2 Fluorotelomer alcohol (6:2 FTOH)
6:2 Fluorotelomersulfonic acid (6:2 FTS)
2,3,3,3-tetrafluoro-2-(heptafluoropropoxy)
-propanoate (GenX)

## Slide 7: Thousands of Chemicals
More Than Just PFOA and PFOS

## Slide 8: Challenges

## Slide 9: Short-chain PFAS
Isotherms of the sorption of different PFAS

## Slide 10: Treatment & Degradation Technologies SWOT Analysis

## Slide 11: Effective PFAS Removal Techniques from Wastewater

## Slide 12: FluorofIX™
      FluorofIX™ is a high-performance ion exchange resin treatment system that removes both long-chain and short-chain PFAS compounds from contaminated water.
      Mobile & modular solution which can treat total PFAS down to non-detect levels, whilst generating minimal waste streams.
      Utilising a series of weak and strong base IX resins which are selected and activated using a proprietary process enabling an extremely high holding capacity for PFAS.
      Dynamic piping and valving designs to allow real-time adjustments to flow and vessel/media priority to ensure complete capacity utilisation & adapt to chemistry variability
      Built-in RegenIX™ compatibility

## Slide 13: Raw Water Characteristics
      PFAS distribution in-line with historical AFFF contamination
      Major regulated compounds (PFOA, PFOS, PFHxS) make up 50% of contamination levels
      Discharge criteria of 0.002µg/L (2ng/L) for sum of PFAS
      90.58% of sulfonic acids present were long chain molecules
      91.26% of Carboxylic acids present were short chain molecules
Chart: Case Study: Average Total PFAS Group Distribution
| Perfluoroalkyl Sulfonic Acids (PFSAs) | Perfluoroalkyl Carboxylic Acids (PFCAs) | Perfluoroalkyl Sulfonamides | n:2 Fluorotelomer Sulfonic Acids (N:2 FTSAs)
% | 0.32542 | 0.16569 | 7.4079e-05 | 0.50882
Case Study: Site Photography
PFAS Group Distribution Averages for Raw Water

## Slide 14: Breakthrough Curves of Regulated Compounds in AU
      PFOA was completely removed below 0.002µg/L after the second filter bank.
      PFOS + PFHxS wasn’t completely removed, but values were below the drinking water guidelines and 95% species regulation after the second filter bank.
Chart: FILTER BANK 2 - SUM OF PFOS + PFHxS
| 191 | 391 | 591 | 991 | 1191 | 1391 | 1591 | 1771 | 2231 | 2391 | 2591 | 2791 | 2991 | 3191 | 3391 | 3591 | 3975.2 | 4175.2 | 4375.2 | 4575.2 | 4775.2 | 4975.2 | 5175.2 | 5375.2 | 5675.2 | 5815.2 | 5975.2 | 6175.2 | 6415.2 | 6575.2 | 6775.2 | 6975.2 | 7175.2 | 7375.2 | 7575.2 | 7775.2 | 7975.2 | 8175.2 | 8375.2000000000007 | 8615.2000000000007 | 8775.2000000000007 | 9015.2000000000007 | 9175.2000000000007 | 9415.2000000000007 | 9575.2000000000007 | 9815.2000000000007 | 9975.2000000000007 | 10175.200000000001 | 10375.200000000001 | 10575.2 | 10775.2 | 10975.2 | 11064.8272
Influent | 8.28 | 23.7 | 25.7 | 18.4 | 17.2 | 28.9 | 21.3 | 20 | 26.9 | 30.2 | 22.4 | 23.6 | 27.4 | 38.5 | 35.5 | 42.6 | 14.5 | 36.2 | 18.7 | 30.1 | 24.4 | 24.1 | 25.7 | 26.6 | 26.8 | 23.5 | 26 | 25.6 | 18.9 | 23.8 | 24.3 | 25.4 | 23.5 | 18.1 | 29 | 40.9 | 72.4 | 33 | 46.9 | 25.6 | 24.7 | 38.7 | 8.28 | 12.7 | 8.52 | 9.12 | 30.4 | 9.93 | 9.15 | 10.1 | 20 | 6.92 | 2.64
Effluent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chart: FILTER BANK 2 - PFOA
| 191 | 391 | 591 | 991 | 1191 | 1391 | 1591 | 1771 | 2231 | 2391 | 2591 | 2791 | 2991 | 3191 | 3391 | 3591 | 3975.2 | 4175.2 | 4375.2 | 4575.2 | 4775.2 | 4975.2 | 5175.2 | 5375.2 | 5675.2 | 5815.2 | 5975.2 | 6175.2 | 6415.2 | 6575.2 | 6775.2 | 6975.2 | 7175.2 | 7375.2 | 7575.2 | 7775.2 | 7975.2 | 8175.2 | 8375.2000000000007 | 8615.2000000000007 | 8775.2000000000007 | 9015.2000000000007 | 9175.2000000000007 | 9415.2000000000007 | 9575.2000000000007 | 9815.2000000000007 | 9975.2000000000007 | 10175.200000000001 | 10375.200000000001 | 10575.2 | 10775.2 | 10975.2 | 11064.8272
Influent | 1.4 | 1.99 | 2.62 | 1.9 | 3.15 | 3.36 | 2.08 | 2.12 | 2.62 | 2.74 | 2.37 | 2.5 | 2.54 | 3.47 | 3.15 | 3.36 | 2.27 | 3.07 | 3.32 | 3.83 | 3.54 | 2.96 | 2.95 | 3.04 | 2.68 | 2.83 | 2.81 | 3.24 | 2.17 | 2.61 | 3.42 | 2.86 | 2.18 | 1.99 | 2.27 | 2.08 | 3.06 | 1.81 | 1.76 | 1.66 | 0.984 | 1.35 | 0.67 | 0.831 | 0.3 | 0.32 | 1.47 | 0.36 | 0.39 | 0.44 | 0.54 | 0.35 | 0.15
Effluent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DWG | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
Chart: FILTER BANK 3 - SUM OF PFOS + PFHxS
| 191 | 391 | 591 | 991 | 1191 | 1391 | 1591 | 1771 | 2231 | 2391 | 2591 | 2791 | 2991 | 3191 | 3391 | 3591 | 3975.2 | 4175.2 | 4375.2 | 4575.2 | 4775.2 | 4975.2 | 5175.2 | 5375.2 | 5675.2 | 5815.2 | 5975.2 | 6175.2 | 6415.2 | 6575.2 | 6775.2 | 6975.2 | 7175.2 | 7375.2 | 7575.2 | 7775.2 | 7975.2 | 8175.2 | 8375.2000000000007 | 8615.2000000000007 | 8775.2000000000007 | 9015.2000000000007 | 9175.2000000000007 | 9415.2000000000007 | 9575.2000000000007 | 9815.2000000000007 | 9975.2000000000007 | 10175.200000000001 | 10375.200000000001 | 10575.2 | 10775.2 | 10975.2 | 11064.8272
Influent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effluent | 0 | 0 | 0.002 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DWG | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07
95% FW Protection | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13
Notes: This slide only pertains to regulated compounds in Australia. I am not sure if there is any value in it for you in the US.
The drinking water guidelines (DWG) indicate that you only need the sum of PFOA under 0.56 ug/L and the sum of PFOS + PFHxS under 0.07 ug/L.
Based on the above-mentioned targets, filter bank 2 (FB2) was good enough for PFOA up to 900 BVs. However, it was not good enough for PFOS + PFHxS, and a third filter bank completed the job in this case.

## Slide 15: Short Chain Removal Performance: Filter Bank 2
Chart: FILTER BANK 2 - PFHpA
| 191 | 391 | 591 | 991 | 1191 | 1391 | 1591 | 1771 | 2231 | 2391 | 2591 | 2791 | 2991 | 3191 | 3391 | 3591 | 3975.2 | 4175.2 | 4375.2 | 4575.2 | 4775.2 | 4975.2 | 5175.2 | 5375.2 | 5675.2 | 5815.2 | 5975.2 | 6175.2 | 6415.2 | 6575.2 | 6775.2 | 6975.2 | 7175.2 | 7375.2 | 7575.2 | 7775.2 | 7975.2 | 8175.2 | 8375.2000000000007 | 8615.2000000000007 | 8775.2000000000007 | 9015.2000000000007 | 9175.2000000000007 | 9415.2000000000007 | 9575.2000000000007 | 9815.2000000000007 | 9975.2000000000007 | 10175.200000000001 | 10375.200000000001 | 10575.2 | 10775.2 | 10975.2 | 11064.8272
Influent | 1.4 | 1.88 | 2.34 | 1.78 | 3.13 | 2.86 | 2.14 | 2.1 | 2.1 | 2.15 | 1.97 | 1.99 | 2.06 | 2.88 | 2.6 | 2.78 | 1.95 | 2.18 | 2.46 | 2.74 | 2.47 | 2.17 | 2.26 | 2.19 | 1.86 | 2.37 | 2.28 | 2.13 | 1.81 | 2.13 | 2.93 | 2.27 | 2.1 | 2.1 | 2.21 | 2.17 | 3.29 | 1.47 | 1.74 | 1.55 | 0.921 | 1.18 | 0.63 | 0.867 | 0.23 | 0.25 | 1.37 | 0.26 | 0.32 | 0.4 | 0.41 | 0.41 | 0.2
Effluent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.04 | 0 | 0 | 0.014 | 0.02 | 0 | 0.02 | 0.02 | 0 | 0 | 0 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04
Chart: FILTER BANK 2 - PFHxA
| 191 | 391 | 591 | 991 | 1191 | 1391 | 1591 | 1771 | 2231 | 2391 | 2591 | 2791 | 2991 | 3191 | 3391 | 3591 | 3975.2 | 4175.2 | 4375.2 | 4575.2 | 4775.2 | 4975.2 | 5175.2 | 5375.2 | 5675.2 | 5815.2 | 5975.2 | 6175.2 | 6415.2 | 6575.2 | 6775.2 | 6975.2 | 7175.2 | 7375.2 | 7575.2 | 7775.2 | 7975.2 | 8175.2 | 8375.2000000000007 | 8615.2000000000007 | 8775.2000000000007 | 9015.2000000000007 | 9175.2000000000007 | 9415.2000000000007 | 9575.2000000000007 | 9815.2000000000007 | 9975.2000000000007 | 10175.200000000001 | 10375.200000000001 | 10575.2 | 10775.2 | 10975.2 | 11064.8272
Influent | 9.55 | 14.2 | 15.9 | 12.4 | 16.8 | 22.8 | 14.2 | 12.5 | 19.6 | 16.3 | 12.8 | 13.5 | 13 | 19.1 | 19.6 | 22 | 12.9 | 17.6 | 15.1 | 16.1 | 16 | 15.9 | 16.4 | 18.8 | 16.3 | 11.9 | 12.3 | 15.1 | 11.4 | 15 | 16.2 | 18.2 | 14.4 | 14.8 | 13.4 | 14.1 | 18.5 | 9.83 | 11.4 | 8.81 | 5.86 | 7.12 | 4.6 | 2.96 | 1.48 | 1.62 | 8.67 | 1.62 | 1.96 | 2.14 | 2.47 | 2.41 | 1.17
Effluent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.06 | 0.04 | 0.07 | 0.11 | 0.11 | 0.16 | 0.2 | 0.21 | 0.27 | 0.727 | 0.52 | 0.67 | 1.36 | 1.52 | 1.38 | 1.68 | 1.66 | 2.04 | 5.54 | 7.3 | 1.96 | 2.91 | 2.77 | 3.97 | 3.06 | 2.11 | 2.77 | 2.62 | 2.54 | 2.66 | 3.01 | 2.32 | 3.12 | 3.84 | 4.56
Chart: FILTER BANK 2 - PFPeA
| 191 | 391 | 591 | 991 | 1191 | 1391 | 1591 | 1771 | 2231 | 2391 | 2591 | 2791 | 2991 | 3191 | 3391 | 3591 | 3975.2 | 4175.2 | 4375.2 | 4575.2 | 4775.2 | 4975.2 | 5175.2 | 5375.2 | 5675.2 | 5815.2 | 5975.2 | 6175.2 | 6415.2 | 6575.2 | 6775.2 | 6975.2 | 7175.2 | 7375.2 | 7575.2 | 7775.2 | 7975.2 | 8175.2 | 8375.2000000000007 | 8615.2000000000007 | 8775.2000000000007 | 9015.2000000000007 | 9175.2000000000007 | 9415.2000000000007 | 9575.2000000000007 | 9815.2000000000007 | 9975.2000000000007 | 10175.200000000001 | 10375.200000000001 | 10575.2 | 10775.2 | 10975.2 | 11064.8272
Influent | 7.47 | 9.33 | 11.6 | 8.42 | 12.1 | 12.2 | 10 | 9.95 | 8.1 | 11.6 | 8.72 | 8.58 | 8.53 | 13 | 14 | 15.3 | 8.48 | 12.8 | 10.2 | 10.8 | 10.4 | 11.3 | 11.4 | 10.9 | 9.92 | 9.11 | 8.99 | 12.8 | 8.02 | 9.81 | 12.9 | 9.14 | 8.61 | 9.3 | 7.48 | 9.28 | 12.2 | 6.66 | 7.79 | 6.16 | 4.15 | 4.3 | 2.76 | 2.31 | 0.97 | 0.99 | 5.99 | 0.92 | 1.08 | 1.47 | 1.56 | 1.44 | 0.91
Effluent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024 | 0.035 | 0.043 | 0.09 | 0.08 | 0.14 | 0.76 | 1.71 | 1.85 | 1.41 | 2.09 | 3.41 | 3.53 | 4.25 | 4.73 | 4.5 | 5.14 | 10.6 | 7.86 | 8.83 | 12.5 | 9.73 | 9.36 | 10.7 | 8.28 | 11.3 | 25.4 | 22.5 | 12.2 | 12.8 | 12.4 | 12.2 | 11.8 | 8 | 8.9 | 7.92 | 6.62 | 7.56 | 7.76 | 6.89 | 8.54 | 8.37 | 9.15
Chart: FILTER BANK 2 - PFBA
| 191 | 391 | 591 | 991 | 1191 | 1391 | 1591 | 1771 | 2231 | 2391 | 2591 | 2791 | 2991 | 3191 | 3391 | 3591 | 3975.2 | 4175.2 | 4375.2 | 4575.2 | 4775.2 | 4975.2 | 5175.2 | 5375.2 | 5675.2 | 5815.2 | 5975.2 | 6175.2 | 6415.2 | 6575.2 | 6775.2 | 6975.2 | 7175.2 | 7375.2 | 7575.2 | 7775.2 | 7975.2 | 8175.2 | 8375.2000000000007 | 8615.2000000000007 | 8775.2000000000007 | 9015.2000000000007 | 9175.2000000000007 | 9415.2000000000007 | 9575.2000000000007 | 9815.2000000000007 | 9975.2000000000007 | 10175.200000000001 | 10375.200000000001 | 10575.2 | 10775.2 | 10975.2 | 11064.8272
Influent | 1.6 | 1.7 | 4 | 2.8 | 4.9 | 5.1 | 3.4 | 3.3 | 2.4 | 3.7 | 3.04 | 2.9 | 2.96 | 4.2 | 4.1 | 3.9 | 1.2 | 3.8 | 3.4 | 3.7 | 2.6 | 3.4 | 3.6 | 3.9 | 3.5 | 3.1 | 3.1 | 3.95 | 2.3 | 2.6 | 3.9 | 1.1 | 3.2 | 3.5 | 3.4 | 3.4 | 4.3 | 2 | 2.5 | 2.2 | 1.22 | 1.6 | 0.9 | 0.86 | 0.3 | 0.3 | 1.6 | 0.2 | 0.19 | 0.4 | 0.4 | 0.5 | 0.1
Effluent | 0 | 0 | 0 | 0.07 | 0 | 0.4 | 0.6 | 0.6 | 1.2 | 1.6 | 1.55 | 1.72 | 2.07 | 3.8 | 3.6 | 4.2 | 2.1 | 6.7 | 6.4 | 4.2 | 3.1 | 5 | 5 | 5.6 | 4.6 | 3.2 | 3.4 | 4.94 | 3.3 | 2.8 | 4.2 | 1.4 | 3.5 | 4.2 | 3.9 | 4.1 | 7.4 | 4.6 | 3.2 | 3.2 | 2.32 | 2.7 | 1.9 | 1.67 | 1.2 | 1 | 0.8 | 0.8 | 0.47 | 0.6 | 0.6 | 0.8 | 0.8
Concentrations of PFBA vs Bed Volumes for filter bank 2
Concentrations of PFPeA vs Bed Volumes for filter bank 2
Concentrations of PFHxA vs Bed Volumes for filter bank 2
Concentrations of PFHpA vs Bed Volumes for filter bank 2
      Short Chain (PFCA’s) responsible for accelerated breakthrough
        PFHpA ~ 7700 BVs
        PFHxA ~ 4000 BVs
        PFPeA ~ 2400 BVs
        PFBA ~ 800 BVs
      The shorter the chain, the faster the breakthrough.
      Filter Bank 3 is designed to tackle short-chain PFAS loading
Notes: This slide is all about the short-chain PFASs, which are mostly carboxylic-based in this fee.
The C4 compound (PFBA) starts leaking sooner than others at around 800 BVs, and dumping occurs at around 3000 BVs.
The C5 compound (PFPeA) is next and starts leaching around 3000 BVs, and dumping occurs around 6500 BDs.
You can follow the lead for the C6 (PFHxA) and C7 (PFHxA) PFASs.

## Slide 16: Short Chain Removal Performance: Filter Bank 2
      FB3 continues to remove “carry over” PFSAs to Non-Detect Levels with intermittent spiking
      Additional FB4 ”polish” treatment step remove carryover compounds
      Designed to ensure Non-Detect discharge during media change out.
      PFCA breakthrough at ~9000 BVs triggering a media changeout
16
Chart: FILTER BANK 3 - SUM OF PFSAs
| 191 | 391 | 591 | 991 | 1191 | 1391 | 1591 | 1771 | 2231 | 2391 | 2591 | 2791 | 2991 | 3191 | 3391 | 3591 | 3975.2 | 4175.2 | 4375.2 | 4575.2 | 4775.2 | 4975.2 | 5175.2 | 5375.2 | 5675.2 | 5815.2 | 5975.2 | 6175.2 | 6415.2 | 6575.2 | 6775.2 | 6975.2 | 7175.2 | 7375.2 | 7575.2 | 7775.2 | 7975.2 | 8175.2 | 8375.2000000000007 | 8615.2000000000007 | 8775.2000000000007 | 9015.2000000000007 | 9175.2000000000007 | 9415.2000000000007 | 9575.2000000000007 | 9815.2000000000007 | 9975.2000000000007 | 10175.200000000001 | 10375.200000000001 | 10575.2 | 10775.2 | 10975.2 | 11064.8272
Influent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.03 | 0 | 0 | 0 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effluent | 0 | 0 | 0.002 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chart: FILTER BANK 3 - SUM OF PFCAs
| 191 | 391 | 591 | 991 | 1191 | 1391 | 1591 | 1771 | 2231 | 2391 | 2591 | 2791 | 2991 | 3191 | 3391 | 3591 | 3975.2 | 4175.2 | 4375.2 | 4575.2 | 4775.2 | 4975.2 | 5175.2 | 5375.2 | 5675.2 | 5815.2 | 5975.2 | 6175.2 | 6415.2 | 6575.2 | 6775.2 | 6975.2 | 7175.2 | 7375.2 | 7575.2 | 7775.2 | 7975.2 | 8175.2 | 8375.2000000000007 | 8615.2000000000007 | 8775.2000000000007 | 9015.2000000000007 | 9175.2000000000007 | 9415.2000000000007 | 9575.2000000000007 | 9815.2000000000007 | 9975.2000000000007 | 10175.200000000001 | 10375.200000000001 | 10575.2 | 10775.2 | 10975.2 | 11064.8272
Influent | 0 | 0 | 0 | 0.07 | 0 | 0.4 | 0.6 | 0.6 | 1.2 | 1.6 | 1.574 | 1.755 | 2.113 | 3.89 | 3.68 | 4.34 | 2.86 | 8.45 | 8.31 | 5.65 | 5.26 | 8.52 | 8.64 | 10.01 | 9.53 | 7.91 | 8.81 | 16.269 | 11.68 | 12.3 | 18.06 | 12.65 | 14.24 | 16.58 | 13.84 | 17.44 | 38.37 | 34.44 | 17.36 | 18.91 | 17.504 | 18.89 | 16.76 | 11.8 | 12.89 | 11.54 | 9.96 | 11.02 | 11.26 | 9.83 | 12.28 | 13.03 | 14.55
Effluent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0.09 | 0 | 0.28 | 0.38 | 0.63 | 0.44 | 0.66 | 0.96 | 1.64
Chart: FILTER BANK 3 - SUM OF PFAS
| 191 | 391 | 591 | 991 | 1191 | 1391 | 1591 | 1771 | 2231 | 2391 | 2591 | 2791 | 2991 | 3191 | 3391 | 3591 | 3975.2 | 4175.2 | 4375.2 | 4575.2 | 4775.2 | 4975.2 | 5175.2 | 5375.2 | 5675.2 | 5815.2 | 5975.2 | 6175.2 | 6415.2 | 6575.2 | 6775.2 | 6975.2 | 7175.2 | 7375.2 | 7575.2 | 7775.2 | 7975.2 | 8175.2 | 8375.2000000000007 | 8615.2000000000007 | 8775.2000000000007 | 9015.2000000000007 | 9175.2000000000007 | 9415.2000000000007 | 9575.2000000000007 | 9815.2000000000007 | 9975.2000000000007 | 10175.200000000001 | 10375.200000000001 | 10575.2 | 10775.2 | 10975.2 | 11064.8272
Influent | 0 | 0 | 0 | 0.07 | 0 | 0.4 | 0.6 | 0.6 | 1.2 | 1.6 | 1.57 | 1.76 | 2.11 | 3.89 | 3.68 | 4.34 | 2.86 | 8.45 | 8.31 | 5.65 | 5.26 | 8.53 | 8.67 | 10 | 9.53 | 7.91 | 8.81 | 16.3 | 11.7 | 12.4 | 18.2 | 12.8 | 14.4 | 16.8 | 14 | 17.7 | 39.1 | 35.7 | 17.6 | 19.3 | 17.8 | 19.4 | 17 | 12.2 | 13.3 | 11.9 | 10.3 | 11.4 | 11.6 | 10.1 | 12.6 | 13.4 | 15
Effluent | 0 | 0 | 0.002 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0.09 | 0 | 0.28 | 0.38 | 0.63 | 0.44 | 0.66 | 0.96 | 1.64
Chart: Sum of PFAS µg/L
| 191 | 391 | 591 | 991 | 1191 | 1391 | 1591 | 1771 | 2231 | 2391 | 2591 | 2791 | 2991 | 3191 | 3391 | 3591 | 3975.2 | 4175.2 | 4375.2 | 4575.2 | 4775.2 | 4975.2 | 5175.2 | 5375.2 | 5675.2 | 5815.2 | 5975.2 | 6175.2 | 6415.2 | 6575.2 | 6775.2 | 6975.2 | 7175.2 | 7375.2 | 7575.2 | 7775.2 | 7975.2 | 8175.2 | 8375.2000000000007 | 8615.2000000000007 | 8775.2000000000007 | 9015.2000000000007 | 9175.2000000000007 | 9415.2000000000007 | 9575.2000000000007 | 9815.2000000000007 | 9975.2000000000007 | 10175.200000000001 | 10375.200000000001 | 10575.2 | 10775.2 | 10975.2 | 11064.8272
Influent | 0 | 0 | 0 | 0.07 | 0 | 0.4 | 0.6 | 0.6 | 1.2 | 1.6 | 1.57 | 1.76 | 2.11 | 3.89 | 3.68 | 4.34 | 2.86 | 8.45 | 8.31 | 5.65 | 5.26 | 8.53 | 8.67 | 10 | 9.53 | 7.91 | 8.81 | 16.3 | 11.7 | 12.4 | 18.2 | 12.8 | 14.4 | 16.8 | 14 | 17.7 | 39.1 | 35.7 | 17.6 | 19.3 | 17.8 | 19.4 | 17 | 12.2 | 13.3 | 11.9 | 10.3 | 11.4 | 11.6 | 10.1 | 12.6 | 13.4 | 15
Effluent | 0 | 0 | 0.002 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0.09 | 0 | 0.28 | 0.38 | 0.63 | 0.44 | 0.66 | 0.96 | 1.64
Case Study One: Concentrations of the sum of PFSAs vs Bed Volumes for filter bank 3
Concentrations of the sum of PFAS vs Bed Volumes for filter bank 3
Case Study One: Concentrations of the sum of PFSAs vs Bed Volumes for filter bank 3
Notes: This slide is all about the short-chain PFASs, which are mostly carboxylic-based in this fee.
The C4 compound (PFBA) starts leaking sooner than others at around 800 BVs, and dumping occurs at around 3000 BVs.
The C5 compound (PFPeA) is next and starts leaching around 3000 BVs, and dumping occurs around 6500 BDs.
You can follow the lead for the C6 (PFHxA) and C7 (PFHxA) PFASs.

## Slide 17: Regeneration
resin

## Slide 18: RegenIX™
      RegenIX™ is SciDev’s IX resin solvent-free regeneration technology, which is integrated into all SciDev’s treatment system designs without significant additional CAPEX costs.
      This approach allows our FluorofIX™ high holding capacity resins to deliver extraordinary PFAS removal performance while optimising RegenIX’s™ ability to restore the resin’s holding capacity and minimising costly IX resin replacement.
      Regenerable ion exchange (IX) resins can have a significantly positive impact on reducing treatment system OPEX and the associated waste generation by minimising the IX resin replacement frequency
      Resin regeneration in PFAS treatment offers an environmental advantage by minimising waste generation, reducing the need for raw materials, and ultimately lessening the carbon footprint associated with disposal

## Slide 19: Degredations | Destruction Technologies
      Thermal Destruction (Incineration)
      Bioremediation
      Chemical Oxidation/Reduction
      Advanced Oxidation/Reduction Process
        Mechanochemical degradation
        Electrochemical degradation
        Sonolysis
        Gamma ray (γ-ray)
        Beams of electrons(eBeam)
        Plasma
        Photolytic degradation

## Slide 20: RegenIX™ Waste Regenerant – Disposal Options
Destruction
Title C Landfill
Incineration
Deep Well Injection
Plasma
Halt
SCWO

## Slide 21: Plasma

## Slide 22: Hydrothermal Alkaline Treatment (HALT)

## Slide 23: Supercritical Water Oxidation (SCWO)

## Slide 24: SWOT Analysis of Destruction Methods

## Slide 25: Mass Balance
To illustrate this distinction, if all perfluorooctanoic acid (PFOA, C8) in a matrix is degraded to perfluoro-heptanoic acid (PFHpA, C7), the technology will have a PFOA degradation efficiency of 100%, a defluorination efficiency of 13% (provided the C−F bonds in the lost CF2 moiety are broken), and a mineralisation efficiency of 0%.
PFOA
PFHpA
-CF2

## Slide 26: Progress

## Slide 27: Production of PFOA and PFOS

## Slide 28: Future…
PFAS remediation spending is forecasted to triple by 2030
For substitution, there are two proposals put forward:
    A universal ban
    A universal ban with use-specific exemptions where there is no known substitute to transition to

## Slide 29
Thank you!
John Wilson Vice-President Water Technologies, Europe john.wilson@scidevltd.com
QUINN SMITH Vice-President Water Technologies, Americas quinn.smith@scidevltd.com
ADAM FARAHANI Technical Manager, Australia adam.farahani@scidevltd.com