## Slide 1
Replacing Missing Instrumentation with Data Science
Murray Callander
Process Engineer
October 20205
Calculating Virtual Flow Rates for Chemical Injection

## Slide 2: The problem
Operator could not see if chemical injection was within spec
No online measurement of chemical injection rates
Could only be checked weekly in hindsight (manual spreadsheet based process)
1st Stage
Test
Subsea manifold
Subsea manifold
Flowline
Flowline
Flowline
A and C wells
B wells
M
M
M
M
Oil rate
Water rate
Oil rate
Water rate
Chemical Injection Point

## Slide 3: Why Accurate Dosing Matters
Overdosing wastes money and causes operational issues
Under-dosing means you do not get the performance
  Depends on the chemical but can be poor separation, corrosion, increased discharge to sea, fouling etc.)
Both under and overdosing demulsifier causes Poor separation
Ideal separation
Notes: Ideal: Clear oil-water separation (bottom: water, top: oil).
Overdosing: Sludge throughout, poor separation, higher oil discharge to sea.
Cause: Wrong dosage, broken pumps, valve faults—too many potential failure points.
Manual calibration only: Using graduated cylinders—a time-consuming, offline process.

## Slide 4: Missing information is chemical flowrate
Periodic manual calibration cylinder for checking rates
These rates were written down on a board next to the injection system.
Could not react to changes in process flow to maintain the dosage.
As-is
To be
Notes: Periodic volumetric measurement
Onshore chemist cannot see what is being dosed offshore
Can only calculate in hindsight

## Slide 5: A clear actionable view
Real-time dashboard shows:
  Chemical concentrations
  Recommended dosage ranges
  Suggested rate adjustments
Traffic light system:
  Green = OK
  Orange = Action required
Engineers can upload Excel sheets to update dosage limits.

## Slide 6: The plan
+
+
Replace manual measurements emailed to shore + weekly spreadsheet with realtime dosage based on change in tank levels plus process flows for 12 tanks/8 chemicals

## Slide 7: Detecting states of flow
Standard Deviation can be used to identify flowing states
Some tanks had a very unstable level signal

## Slide 8: Tuning the data analytics
Define a period for each tank over which instability is “cancelled” – i.e. we can clearly differentiate between states
Use combination of STDDEV & DIFFERENTIAL to identify features

## Slide 9: Identifying tank flowing state
Use combination of STDDEV & DIFFERENTIAL to identify features
Need to derive clear separation of states to avoid “chattering”
Flowing when STDDEV above this level
And DIFF below this level

## Slide 10: Dealing with real data
The real data was extremely noisy

## Slide 11: 1hr STDDEV and DIFF is too unstable

## Slide 12: Lowpass filter improves signal
10 min window
60 min window

## Slide 13: Lowpass vs Average
60 min Lowpass filter gives better smoothing for our case. This ”feature” remains in the average but it is not real* and causes us problems
* This would imply a top-up of approx. 2 litres which is not possible

## Slide 14: Combining LOWPASS with DIFF gives clear separation

## Slide 15: Live version
Runs every 5 minutes
Calculates the flowrates based on sliding window
Window size is chosen to smooth out instability
Good for responding quickly to changes offshore
Susceptible to variability – not so useful for historic analysis

## Slide 16: Hindsight version
Event based
Very accurate
Calculates the flowrates for complete episodes
Only calculates the flowrate at the end of an episode
Excellent for retrospective analysis
Cannot be used to detect changes in realtime

## Slide 17: Combining the two

## Slide 18: Calculating the dosage in ppm
Simple in principle:
In practice there are several steps
All of it is done in an online calculation to create a soft tag (virtual timeseries)
Which tank is flowing
Convert to m3
Add 3 process flows (water)
Calculate dosage
Smooth it with an average
Clamp it to zero because FI’s show small flow when there is none

## Slide 19: Calculating recommended dosage in l/h
Simple in principle:
Again, it is done in an online calculation to create a soft tag (virtual timeseries)
Downhole Scale Inhibitor was a big calculation!
  Sum(the water rate from the last well test if the well is online)

## Slide 20: Calcs are saved with an alias for easy access by anyone – same as a “real” sensor

## Slide 21: Operational Benefits
Save time:
Shortens the time of response when the dosing is getting out of the desired range from 1 week to 2-4 hours.
One source of truth:
The data can be found in one place and seen in a single view instead of several tabs in a spreadsheet.
Troubleshooting aid:
Early detection of equipment issues (pumps, valves). Identify when flowmeters require calibration.
Instant actions:
No longer dependent on a single person or onshore-only access. Offshore operators can act immediately: Take a photo or print the recommendation.

## Slide 22: Thank you!
For any further queries, email us at info@eigen.co